一分钟了解丨你的产品在不在BS476-7防火测试要求内

BS 476-7 是英国关于建筑材料和结构的着火试验标准中，用于测定产品火焰表面延伸等级的测试方法。

标准要求的产品范围：

BS 476-7防火测试适用于各种类型的建筑材料和制品，包括墙壁、天花板、地板、隔墙、门、窗框、绝缘材料等，主要用于测定墙面、保温材料、天花板等建筑材料暴露表面的火焰延伸情况。

常见的测试材料包括：

玻璃钢，塑料件，显示屏，墙板，各类型板材，岩棉，发泡等

备注：之前香港显示屏发生了火灾，故而目前要销往香港的显示屏都会要求做BS476-7防火测试。

BS 476-7是怎么测试的呢？

测试步骤如下：

- 点燃引燃火焰

- 在 5 秒时间内，摆动样品夹，并放到测试位置上，接下来立即开启定时机构，也就是开始测试。

- 在测试开始后一分钟内熄灭引燃火焰。

- 在火焰头达到 825 毫米的参考线时，或经过 10 分钟后，无论哪一个更短都要停止该测试。

BS476-7等级判定：

| 级别 | 试验1.5min时的火焰传播程度 |  | 试验终了时的火焰传播程度 |  |
| --- | --- | --- | --- | --- |
|  | 极限值mm | 允许偏差值mm | 极限值mm | 一个试件允许偏差值mm |
| 1 | 165 | 25 | 165 | 25 |
| 2 | 215 | 25 | 455 | 45 |
| 3 | 265 | 25 | 710 | 75 |
| 4 | 超过3级的值 |  |  |  |

Find out in one minute whether your product meets the fire test requirements of BS476-7

BS 476-7 is a test method for determining the surface extension level of flames in the UK fire test standard for building materials and structures.

Product range required by the standard:

BS 476-7 fire test is applicable to various types of building materials and products, including walls, ceilings, floors, partitions, doors, window frames, insulation materials, etc. It is mainly used to determine the flame extension of exposed surfaces of building materials such as walls, insulation materials, ceilings, etc.

Common test materials include:

Glass fiberglass, plastic parts, display screens, wall panels, various types of panels, rock wool, foam, etc.

Note: There was a fire in the display screen in Hong Kong before, so the display screens to be sold to Hong Kong are required to undergo BS476-7 fire test.

How is BS 476-7 tested?

The test steps are as follows:

1) Ignite the pilot flame

2) Within 5 seconds, swing the sample clamp and put it in the test position, and then immediately start the timing mechanism, that is, start the test.

3) Extinguish the pilot flame within one minute after the test starts.

4) The test shall be stopped when the flame head reaches the 825 mm reference line, or after 10 minutes, whichever is shorter.